## Introduction
Table of Minimum Offsets
The following table of offsets gives the minimum required offsets for infrastructure across the major reviewing sections. Each tab is all-inclusive, meaning that all the offsets are self-contained in each tab. We have several tabs to facilitate ease of use, so if a surface drawing is being drafted or reviewed then the Complete Streets tab can be used easily, or if a landscaping drawing is being drafted or reviewed then the Landscaping tab can be used. These offsets are applicable to most cases. However, they may vary for infill or non-standard situations as existing conditions may require unique offsets, as determined by the City.
A design exception may be necessary to facilitate an implementable design or to introduce a non-traditional or alternative design that offers significantly improved performance. The Consolidated Design Exception Form will be utilized to evaluate and determine the performance, risk and mitigation strategies for design exceptions across Volumes 2, 3, 4, 5, 6 and 7 of the City and EPCOR Design and Construction Standards. This consolidated form replaces the individual design exception forms that were in use previously.
DISCLAIMER:
All information in this Table of Offsets has been gathered and amalgamated from Volumes 2,3,4,5,6 and 7 of the City and EPCOR Design and Construction Standards. Specific source volumes are specified in each tab of this workbook. As such, this is information only and does not require engineering authentication.

## Version History
Version History
September 17, 2025 Version:
Addition of the Consolidated Design Exception Form
July 2, 2025 Version:
Various changes to EPCOR Water offsets to update offsets per new updated EPOR Water Standards
January 14, 2022 Version:
Disclaimer added and source volumes. Minor format changes.
June 30, 2021 Version:
Added "DPS" tab for Distribution Piping Systems for capital projects only
April 28, 2021 Version:
Various changes to EPCOR Water offsets to update offsets per new updated EPOR Water Standards
Pre April 28, 2021 version:
Originally released Table of Offsets

## Complete Streets
Domain: Complete Streets (Volume 2)
Subdomain: Complete Streets (Volume 2)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes | Data Source (Volumes from Standards)
Intersection edge of pavement | Traffic control cabinet | Located outside the Clear Sight Triangles to allow for required sightlines |  | 2
Commercial/Industrial access edge of pavement | Traffic control cabinet | 10.0m
Curb Ramps | Commercial Crossing | 1.0m | Flare to flare
Shared-use paths, walkways, and sidewalks | Property line | 0.3m | Property line to edge of shared-use path, walkway, or sidewalk
Subdomain: EPCOR Drainage (Volume 3)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Face of Curb | Sanitary and storm mains | 1.5m |  | 2,3
Curb Ramps | Catchbasins and catchbasin manholes | 0.5m
Bus stop pad | Storm and sanitary services | 1.5m | 1.5 m from the edge of the bus stop pad, Drainage prefers sewer services to not to be buried under the bus stop pad
Driveways | Catchbasins | 1.5m | Edge of driveway.
Intersection | Catchbasins | Locate at End of Curve OR Beginning of Curve and not within the curb ramp and crosswalk
Subdomain: EPCOR Water (Volume 4)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
PL | Curb cock | 0.1m | 0.3m from PL for side lot services | 2,4
Face of Curb (FOC) | Watermain | 1.5m (<= 400 mm mains)
FOC | Watermain | 2.0m (> 400 mm mains)
PL | Watermain in alley, utility lot, walkway, or URW | 1.2m (preferably 2.0m) | Mains in walkways are to be dimensioned to side PL.
PL | Water services | Extend service into lot 1.5m beyond the edge of the shallow utility easement | If the water service enters a parcel where there isn't a shallow utility easement, the water service shall extend into the lot a minimum of 1.5m beyond the property line.
PL | Flushpoint | 1.5m | Plug is 5.0m from PL
FOC | Hydrant | Preferred: 3.0m for any ROW with Monowalk. Min 1.5 m - max 3.5 m offset acceptable. | If the monolithic walk is greater than 2.5 m wide, include a 90 degree bend in the hydrant lead and locate the hydrant and the control valve 0.3 m behind the back edge of the walk.
FOC | Hydrant | 1.5m for any ROW with Separate Walk | Where the walk is greater than 2.0 m into the boulevard or where no walk exists.
Edge of Walk | Hydrant | 0.3m
Edge of Bus Stop | Hydrant | 6.0m | Hydrants located within 45 m of the approach side of the bus stop or 15 m of the departure side must be labeled "To be white disked (Fire Dept. Use Only) at commissioning."
Edge of Driveway | Hydrant | To be located on the opposite lot line from driveway | If unable, minimum 1.5m (preferably 2.0m)
Corner of intersection | Hydrant | To be installed at the beginning of the curve of the curb return | Where not in conflict with item 4.2.14.
Alley | Valves | 6.0m of the approach & 3.0m of the departure
Arterial road & collector road intersection | Valves | 30m (edge to edge)
Property Line | Valves | To be located on the projection of PL, where possible or dimension to a PL
Utility lot, walkway or URW | Valves | 0.5m from PL or its projection
Subdomain: Landscaping (Volume 5)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
FOC (local) | Trees (centre of tree) | 1.0m, 1.25m preferred | Trees to be placed in line with or further from Face of Curb than Streetlight Poles. | 2,5
FOC (Collector) | Trees (centre of tree) | 1.25m / 1.65m | 1.25 m ROW < 20m, 1.65 m ROW > 20m. Trees to be placed in line with or further from Face of Curb than Streetlight Poles.
FOC (Arterial) | Trees (centre of tree) | 2.0m | Trees to be placed in line with or further from Face of Curb than Streetlight Poles.
Intersection | Trees (centre of tree) | 15m
Edge of Sidewalk, Driveway, Walkway, and Shared-Use Path | Trees (centre of tree) | 1.0m, preferred 1.5m
Edge of Sidewalk, Walkway and Shared-Use Path | Shrubs | 0.5m | Shrubs at maturity
Edge of walk | Litter receptacle | 0.6m
Edge of commercial or industrial access | Trees (centre of tree) | 1.5m
Back of walkway | Benches | 1.0m
Back of walkway | Picnic Table | 1.0m
Boulevard curb | Mulched beds | 2.5m | Within boulevard curb along arterial and collector roadways.
Stop signs and yield signs | Trees (centre of tree) | 3.5m
All other signs | Trees (centre of tree) | 2.0m
Transit zones/bus pads | Trees (centre of tree) | 3.5m | In addition to the 3.5 m clearance, ensure trees do not create sightline obstructions for vehicles approaching transit zones.
Property line | Trees (centre of tree, in walkway or shared-use path ROW) | 1.0m
Property line | Trees (centre of tree, in boulevard) | 1.0m
Property Line | Deciduous trees (in open parkland) | 2.5m | From centre of tree, in open parkland where there is turf between the fence and the tree rather than a bed.
Property Line | Coniferous trees (in open parkland) | 2.5m | From edge of mature spread of tree, in open parkland where there is turf between the fence and the tree rather than a bed.
Subdomain: Streetlighting (Volume 6)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
FOC | Streetlight Pole (centre of pole) | 1.25m along Local Streets; 1.25m along Collectors; 2.0m along Arterials; 2.6m for monowalks along Local and Collector Streets, 3.0m for monowalks adjacent to School Sites |  | 2,6
FOC | Multiparty trench | 2.5m | Centerline of trench
Intersection | Streetlight Pole (centre of pole) | 0.9m
Edge of sidewalk or walkway | Streetlight Pole (centre of pole) | 0.5m / preferred 1.0m
Edge of shared-use paths | Streetlight Pole (centre of pole) | 0.5m / preferred 1.5m
Driveway (Residential) | Streetlight Pole (centre of pole) | 0.5m with standard base and 0.75m with utility box
Driveway/Access (Commerical or Industrial) | Streetlight Pole (centre of pole) | 1.5m
Subdomain: EPCOR Power (Volume 7)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
FOC | Multiparty trench | 2.5m | Centerline of trench | 2,7
FOC | Transformer | SEE NOTES | Offset is required. See the specific and applicable cross-section(s) found in Complete Streets Design and Construction Standards.
Corner cut | Power crossings | 3.0m
Corner cut | Transformer | 6.0m
Corner cut | 1-phase or 3-phase cubicle | 30m
Bus stop pad | Transformer/Switching cubicle | 3.0m | From edge of bus pad to edge of base
Road crossing | Transformer/Switching cubicle | 3.0m | From centre to closest duct in crossing
Transportation control devices and signs | Pad-mounted equipment | 3.0m | From edge of pad
Bus stop pad | Power crossings | 3.0m | From edge of bus pad to crossing
Residential driveways | Transformer | 2.0m | From edge of equipment to driveway
Intersection edge of pavement | Transformer/Switching cubicle | 15m | From centre of transformer/switching cubicle
Commercial/Industrial access edge of pavement | Transformer/Switching cubicle | 10m
Edge of walkway property line | Pad-mounted equipment | 3.0m | From edge of equipment to edge of walkway property line
PL | Main power/Multiparty trench | 1.0m | Actual required minimum offset may change depending on sidewalk type and alignmnt of shallow utilities.
Subdomain: Gas
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
FOC | Multiparty trench | 2.5m | Centerline of trench | 2
Subdomain: Telecommunications
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
FOC | Multiparty trench | 2.5m | Centerline of trench | 2
Subdomain: General
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Location of all surface appurtenances associated with underground utilities (including, but not limited to, transformers, cubicles, catch basins, manholes and utility covers, water valves, power/telecom vaults) | Active Transportation Infrastructure | Located outside of any sidewalks, shared-use paths, walkways, crosswalks, and curb ramps; See also the City’s Design and Construction Standards Volumes 3, 4, and 7 |  | 2

## EPCOR Drainage
Domain: EPCOR Drainage (Volume 3)
Subdomain: Complete Streets and Roadways (Volume 2)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes | Data Source (Volumes from Standards)
Storm and sanitary mains | Face of Curb | 1.5m |  | 2,3
Storm and sanitary services | Bus stop pad | 1.5m | 1.5 m from the edge of the bus stop pad, Drainage prefers sewer services are not to be buried under the bus stop pad
Catchbasins and catchbasin manholes | Curb Ramps | 0.5m
Catchbasins | Driveways | 1.5m | Edge of driveway.
Catchbasins | Intersection | Locate at End of Curve OR Beginning of Curve and not within the curb ramp and crosswalk
Subdomain: EPCOR Water (Volume 4)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Sanitary & Storm Main | Watermain | 2.5m (preferably 3.0m) | Additional clearance may be required at the Engineer's (EWSI) discretion, including when pipe diameters are greater than 300 mm. | 3,4
Sanitary Main, Storm Main and Catch Basin Leads Crossing | Watermain | 0.3 m when crossing under water main (edge to edge) 0.5 m when crossing over water main (edge to edge) | Catch basin leads must be shown where they cross water mains.
MH | Watermain | 2.5m
Oversized MH (Ø1800 & larger) | Watermain | 3.0m | From the centreline to centreline (watermains <= 600 mm)
Catch Basin | Watermain | 1.5m
Catch Basin lead | Watermain | 2.5m (preferably 3.0m)
Storm Sanitary service | Watermain | 2.5m (preferably 3.0m) | When paralleling main
Storm and Sanitary service crossing | Watermain | 0.15m (edge to edge) | Vertical Crossing
Storm Sanitary service | Large water service, Ø100 & larger | 3.0m | Provide dimension from PL to services. Large water service to be in own trench.
Storm Sanitary service | Water Services (50mm and smaller) | 0.3 m | For typical dual and single services for single family, duplex, and semi-detached lots. Services 50mm and smaller to be laid in same trench as storm and sanitary services, to the right of the sanitary service when facing lot to be served. Water services 100mm and larger to be treated as watermains
MH shaft | Water Services (50mm and smaller) | 2.0m | Water services 100mm and larger to be treated as watermains
Catch Basin | Water Services (50mm and smaller) | 2.5m | Water services 100mm and larger to be treated as watermains
Catch Basin lead | Water Services (50mm and smaller) | 2.5m | Water services 100mm and larger to be treated as watermains
Storm and Sanitary Main | Water Services (50mm and smaller) | 1.5m (2.5m preferred) | For small services only (50mm and smaller). When paralleling. Water service cannot be between a storm main and a sanitary main. Water services 100mm and larger to be treated as watermains
Storm and Sanitary joint | Water Services (50mm and smaller) | 1.5m | Clearance is from joint, not centre of fitting (tee, cross, bend, etc.) Water services 100mm and larger to be treated as watermains
Storm and Sanitary service | Hydrants | 2.5m
CB lead | Valve | 3.0m
Drainage Infrastructure or non-potable water infrastructure | Infrastructure with a thrust block (reducer, tee, cross or bend) | 1.5m
Drainage Infrastructure or non-potable water infrastructure including storm and sanitary services | Water Joint | 1.5m | Clearance is from the joint not from the center of fitting (tee, cross, bend, etc.). Clearance also applies to tie in joints (i.e. plugs after BVs).
Storm inline tee/ sanitary core-bell insert and service line | Water mainstop | 0.3m
Subdomain: Landscaping (Volume 5)
Domain Infrastructure | Minimum Clearance | Minimum Clearance | Minimum Clearance
Storm and sanitary services | Trees | 1.8m | Centre of tree | 3,5
Storm and sanitary manholes | Trees | 1.8m | Centre of tree
Subdomain: Streetlighting (Volume 6)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Storm and sanitary services | Streetlights and power poles | 2.0m |  | 3,6
Subdomain: EPCOR Power (Volume 7)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Drainage/Sanitary Main, Catch basin, manhole, vault other large drainage structure | Main power trench | 2.0m | Troughed to 1.5 m either side of catch basin if less than 2.0 m | 3,7
Manhole, catch basin, storm and sanitary services | 1-phase pad-mounted equipment | 4.5m | 3.0 m is required from the ground grid to the other utility
Manhole, catch basin, storm and sanitary services | 3-phase pad-mounted equipment | 5.0m | 3.0 m is required from the ground grid to the other utility
Catch basin, storm and sanitary services | Power crossings | 3.0m | Crossings in roadways must be 3.0 m from catch basins
Subdomain: Gas
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Storm and sanitary mains | Gas crossings and line | Minimum 1.5m, preferred 3.0m |  | 3
Storm and sanitary services | Gas crossings and line | Minimum 1.5m, preferred 3.0m
Catchbasins and catchbasin manholes | Gas crossings and line | Minimum 1.5m, preferred 3.0m
Subdomain: Telecommunications
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Storm and sanitary mains | Telecommunications pedestal and line | Minimum 1.5m, preferred 3.0m |  | 3
Storm and sanitary services | Telecommunications pedestal and line | Minimum 1.5m, preferred 3.0m

## EPCOR Water
Item Number | Domain: EPCOR Water (Volume 4)*
4.2 | Subdomain: Complete Streets (Volume 2)
| Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance **(Unless otherwise specified) | Notes | Data Source (Volumes from Standards)
4.2.1 | Curb cock | PL | 0.1m | 0.3m from PL for side lot services | 2,4
4.2.2 | Watermain | Face of Curb (FOC) | 1.5m (<= 400 mm mains)
4.2.3 | Watermain | FOC | 2.0m (> 400 mm mains)
4.2.4 | Watermain in alley, utility lot, walkway, or URW | PL | 1.2m (preferably 2.0m) | Mains in walkways are to be dimensioned to side PL.
4.2.5 | Water services (50mm and smaller) | PL | Extend service into lot 1.5m beyond the edge of the shallow utility easement | Water services 100mm and larger to be treated as watermains. If the water service enters a parcel where there isn't a shallow utility easement, the water service shall extend into the lot a minimum of 1.5m beyond the property line.
4.2.6 | Flushpoint | PL | 1.5m | Plug is 5.0m from PL
4.2.7 | Hydrant | FOC | Preferred: 3.0m for any ROW with Monowalk. Min 1.5m - max 3.5m offset acceptable. | If the monolithic walk is greater than 2.5m wide, include a 90 degree bend in the hydrant lead and locate the hydrant and the control valve 0.3m behind the back edge of the walk.
4.2.8 | Hydrant | FOC | 1.5m for any ROW with Separate Walk | Where the walk is greater than 2.0 m into the boulevard or where no walk exists.
4.2.9 | Hydrant | Edge of Walk | 0.3m
4.2.10 | Hydrant | Edge of Bus Stop | 6.0m | Hydrants located within 45m of the approach side of the bus stop or15 m of the departure side must be labeled "To be white disked (Fire Dept. Use Only) at commissioning."
4.2.11 | Hydrant | Edge of Driveway | To be located on the opposite lot line from driveway | If unable, minimum 1.5m (preferably 2.0m)
4.2.12 | Hydrant | Corner of intersection | To be installed at the beginning of the curve of the curb return | Where not in conflict with item 4.2.14.
4.2.13 | Valves | Alley | 6.0m of the edge of approach & 3.0m of the edge of departure
4.2.14 | Valves | Arterial road & collector road intersection | 30m (edge to edge)
4.2.15 | Valves | Property Line | To be located on the projection of PL, where possible or dimension to a PL
4.2.16 | Valves | Utility lot, walkway or URW | 0.5m from PL or its projection
4.3 | Subdomain: EPCOR Drainage (Volume 3)
| Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance **(Unless otherwise specified) | Notes
4.3.1 | Watermain | Sanitary & Storm Main | 2.5m (preferably 3.0m) | Additional clearance may be required at the Engineer's (EWSI) discretion, including when pipe diameters are greater than 300mm. | 3,4
4.3.2 | Watermain | Sanitary Main, Storm Main and Catch Basin Leads Crossing | 0.3m when crossing under water main (edge to edge) 0.5m when crossing over water main (edge to edge) | Catch basin leads must be shown where they cross water mains.
4.3.3 | Watermain | MH | 2.5m
4.3.4 | Watermain | Oversized MH (Ø1800 & larger) | 3.0m | From the centreline to centreline (watermains <= 600mm)
4.3.5 | Watermain | Catch Basin | 1.5m
4.3.6 | Watermain | Catch Basin lead | 2.5m (preferably 3.0m)
4.3.7 | Watermain | Storm Sanitary service | 2.5m (preferably 3.0m) | When paralleling main
4.3.8 | Watermain | Storm and Sanitary service crossing | 0.15m (edge to edge) | Vertical Crossing
4.3.9 | Large water service, Ø100 & larger | Storm Sanitary service | 3.0m | Provide dimension from PL to services. Large water service to be in own trench.
4.3.10 | Water Services (50mm and smaller) | Storm Sanitary service | 0.3m | For typical dual and single services for single family, duplex, and semi-detached lots. Services 50mm and smaller to be laid in same trench as storm and sanitary services, to the right of the sanitary service when facing lot to be served. Water services 100mm and larger to be treated as watermains
4.3.11 | Water Services (50mm and smaller) | MH shaft | 2.0m | Water services 100mm and larger to be treated as watermains
4.3.12 | Water Services (50mm and smaller) | Catch Basin | 2.5m | Water services 100mm and larger to be treated as watermains
4.3.13 | Water Services (50mm and smaller) | Catch Basin lead | 2.5m | Water services 100mm and larger to be treated as watermains
4.3.14 | Water Services (50mm and smaller) | Storm and Sanitary Main | 1.5m (2.5m preferred) | For small services only (50mm and smaller). When paralleling. Water service cannot be between a storm main and a sanitary main. Water services 100mm and larger to be treated as watermains
4.3.15 | Water Services (50mm and smaller) | Storm and Sanitary joint | 1.5m | Clearance is from joint, not centre of fitting (tee, cross, bend, etc.) Water services 100mm and larger to be treated as watermains
4.3.16 | Hydrants | Storm and Sanitary service | 2.5m
4.3.17 | Valve | CB lead | 3.0m
4.3.18 | Infrastructure with a thrust block (reducer, tee, cross or bend) | Drainage Infrastructure or non-potable water infrastructure | 1.5m
4.3.19 | Water Joint | Drainage Infrastructure or non-potable water infrastructure including storm and sanitary services | 1.5m | Clearance is from the joint not from the center of fitting (tee, cross, bend, etc.). Clearance also applies to tie in joints (i.e. plugs after BVs).
4.3.20 | Water mainstop | Storm inline tee/ sanitary core-bell insert and service line | 0.3m
4.4 | Subdomain: General / EPCOR Water (Volume 4)
| Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance **(Unless otherwise specified) | Notes
4.4.1 | Watermain | Watermain | 1.5m | If the carriageway allows for two water mains to be located within the street or avenue. | 4
4.4.2 | Watermain | Any other utility crossing the water main | 1.0m vertical (edge to edge) | Does not include storm and sanitary sewer mains and DPS mains.
4.4.3 | Tapping Valve Sleeve (TVS) - 300mm or smaller | All pipe joints, including other appurtenances, including other tapped valves | 1.0m
4.4.4 | Tapping Valve Sleeve (TVS) - 350mm or larger | All pipe joints, including other appurtenances, including other tapped valves | 1.5m
4.4.5 | Water mainstop | To other mainstop including adjacent bell, collar, plug or coupling | 0.6m
4.4.6 | Water mainstop | From any water joint i.e., bend, tee, cross, valves, etc. | 0.6m
4.4.7 | Water mainstop | Storm inline tee/ sanitary core-bell insert and service line | 0.3m
4.4.8 | Water Main and Any Utility Crossing | Deflection or joint on either utility (including water main) | 1.5m horizontal separation | All crossings shall be at 90 degrees to the water infrastructure. If this cannot be achieved, the crossing shall not be at an angle of less than 45 degrees.
4.5 | Subdomain: Landscaping (Volume 5)**
| Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
4.5.1 | All water infrastructure | Soil cells | See Volume 4 Section 1.15 |  | 4,5
4.5.2 | Valve, hydrant, curb cock (CC), or watermain | Fence | 1.2m | For fencing on private property, offset for fencing on public property will be at 1.2m or greater, at the discretion of the City.
4.5.3 | Watermains, services, manual air vents | Deciduous tree | 1.8m | Ensure that these dimensions are measured from the actual service locations and not the property line.
4.5.4 | Watermains, Services, manual air vents | Coniferous tree | 3.5m | Ensure that these dimensions are measured from the actual service locations and not the property line.
4.5.5 | Hydrant | Deciduous tree | 3.5m
4.5.6 | Hydrant | Coniferous tree | 7.0m
4.5.7 | Hydrant | Shrubs | 1.0m behind hydrant and 1.5 m on either side of the hydrant (extending to road)
4.5.8 | Valve, hydrant, curb cock (CC), or watermain | Movable street and parks furniture including but not limited to benches, tables, and waste receptacles | 1.5m
4.5.9 | Valve, hydrant, curb cock (CC), or watermain | Immovable street and parks furniture including but not limited to signs, public art, and retaining walls | 3.0m
4.5.10 | Provide a dimension from the landscaping element to the water appurtenance if: Within 3.0m of water service Within 5.0m of valve, hydrant or curb cock or any other infrastructure
4.6 | Subdomain: Streetlighting (Volume 6)
| Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
4.6.1 | Hydrant | Streetlight pole (centre of pole) | 1.8m | Edge to edge with pedestal, transformer, telecommunication cubicles & streetlightlight poles | 4,6
4.6.2 | Water services (50mm and smaller) | Streetlight pole (centre of pole) | 1.8m | Water services 100mm and larger to be treated as watermains
4.6.3 | Watermain | Streetlight pole (centre of pole) | 1.8m
4.7 | Subdomain: EPCOR Power (Volume 7)
| Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
4.7.1 | Water services and hydrants/flush points/air vents | 1-phase pad-mounted equipment | 4.5m |  | 4,7
4.7.2 | Water services and hydrants/flush points/air vents | 3-phase pad-mounted equipment | 5.0m
4.7.3 | Water services (50mm and smaller) | Power services and Power Cables Paralleling Water Service | 1.8m | Clearance is from the actual water service location, not from the water service symbol. Water services 100mm and larger to be treated as watermains
4.7.4 | Valves and curb cocks | Power cables <= 40 kV | 1.0m | Minimum distance between CC and any power cables. Telecommunication cables, gas mains, duct lines
4.7.5 | Valve or water appurtenances is crossed on both sides | Power cables <= 40 kV | 1.8m
4.7.6 | Valve casings | Pad-mounted equipment | 1.5m | Edge to edge
4.7.7 | Hydrants with control valves more than 2m from hydrant | Power cables <= 40 kV crossing between control valve and hydrant | Hydrants: 3m Valves 1.0m | Hydrant: 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
4.7.8 | Hydrants | Main power cable and duct bank | 3.0m | See EDTI Standard for Trenching Around Hydrants for reduced clearances (Volume 7: EDTI Standards)
4.7.9 | Hydrants | Power cables <= 40 kV | 3.0m | 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
4.7.10 | Watermain | Secondary Power Cable (<=750 V) | 2m from edge of pipe | Water services 100mm and larger to be treated as watermains
4.7.11 | Watermain and Water services | Primary Power Cable (<=40 kV) | 4m from edge of pipe | Primary power to be located on opposite side of the road unless power is in a four party trench or otherwise approved by the Engineer.
4.7.12 | Watermain and Water services | High Voltage Power Cable (>40 kV) | See Notes | To be designed based on safe limits of approach and excavation allowance.
4.7.13 | Watermain | Pad-mounted equipment | 3.0m
4.7.14 | All water infrastructure | Grounding rods | 1.8m
4.7.15 | Watermain and Water services | Power poles, pole anchors | 1.8m
4.8 | Subdomain: Gas
| Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
4.8.1 | Watermain | Gas main | 1.8m |  | 4
4.8.2 | Valve or curb cock (CC) | Gas mains or ductlines | 1.0m
4.8.3 | Valve or water appurtenances is crossed on both sides | Gas mains or ductlines | 1.8m
4.8.4 | Hydrant | Gas mains or ductlines | 1.5m | 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
4.8.5 | Hydrants with control valves more than 2m from hydrant | Gas mains or ductlines crossing between control valve and hydrant | Hydrants: 3m Valves 1.0m | Hydrant: 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
4.8.6 | Water services (50mm and smaller) | Gas services and gas crossings | 1.8m | Clearance is from the actual water service location, not from the water service symbol Water services 100mm and larger to be treated as watermains
4.8.7 | Water services (50mm and smaller) | Gas mains or ductlines | 1.8m | Water services 100mm and larger to be treated as watermains
4.9 | Subdomain: Telecommunications
| Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes | 4
4.9.1 | Watermain | Telecommmunication cable, cubicles, poles and pedestals | 1.8m
4.9.2 | Valve or curb cock (CC) | Telecommmunication cable | 1.0m
4.9.3 | Hydrant | Telecommmunication cable | 1.5m | 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
4.9.4 | Valve or water appurtenances is crossed on both sides | Telecommmunication cable | 1.8m
4.9.5 | Hydrants with control valves more than 2m from hydrant | Telecommunication cable crossing between control valve and hydrant | Hydrants: 3m Valves 1.0m | Hydrant: 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
4.9.6 | Water services (50mm and smaller) | Telecommmunication cable, cubicles, poles and pedestals | 1.8m | Water services 100mm and larger to be treated as watermains
* Table of Offsets provided assuming existing PVC water pipe (</= 300 mm), proximity to other pipe materials subject to EPCOR Water Services review and may require increased clearances. All clearances are center to center unless otherwise specified.
** Dimension symbol and legend can be used instead of dimension line to avoid clutter.

## DPS
Domain: DPS Systems (Volume 1)* (SEE ADDITIONAL NOTES AT THE BOTTOM)
Subdomain: Complete Streets (Volume 2)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance *(Unless otherwise specified) | Notes | Data Source (Volumes from Standards)
Curb cock | PL | 0.1m | 0.3m from PL for side lot services | District Energy Sharing Systems Standards, 2
DPS Main/Branch | Face of Curb (FOC) | 1.5m (<= 400 mm mains)
DPS Main/Branch | FOC | 2.0m (> 400 mm mains)
DPS Main/Branch in alley, utility lot, walkway, or URW | PL | 1.2m (preferably 2.0m) | Mains in walkways are to be dimensioned to side PL.
DPS Services | PL | Extend service into lot a minimum of 1.5m beyond the edge of the shallow utility easement | If the DPS service enters a parcel where there isn't a shallow utility easement, the DPS service shall extend into the lot a minimum of 1.5m beyond the property line.
Blow-off/Drain Manhole | PL | 1.5m from centerline of blow-off air vent to PL
Valves | Alley | 6.0m of the approach & 3.0m of the departure
Valves | Arterial road & collector road intersection | 30m
Valves | Property Line | To be located on the projection of PL, where possible or dimension to a PL
Valves | Utility lot, walkway or URW | 0.5m from PL or its projection
Subdomain: EPCOR Drainage (Volume 3)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance *(Unless otherwise specified) | Notes
DPS Main/Branch | Sanitary & Storm Main | 2.5m (preferably 3.0m) | Additional clearance may be required at the Engineer's discretion, including when pipe diameters are greater than 300 mm. | District Energy Sharing Systems Standards, 3
DPS Main/Branch | Sanitary Main, Storm Main and Catch Basin Leads Crossing | 0.3 m when crossing under DPS main/branch 0.5 m when crossing over DPS main/branch | Catch basin leads must be shown where they cross DPS main/branch.
DPS Main/Branch | MH | 2.5m
DPS Main/Branch | Oversized MH (Ø1800 & larger) | 3.0m | From the centreline to centreline (DPS main/branch <= 600 mm)
DPS Main/Branch | Catch Basin | 1.5m
DPS Main/Branch | Catch Basin lead | 2.5m (preferably 3.0m)
DPS Main/Branch | Storm Sanitary service | 2.5m (preferably 3.0m) | When paralleling main
DPS Main/Branch | Storm and Sanitary service crossing | 0.15m | Vertical Crossing
DPS service, Ø100 & larger | Storm Sanitary service | 3.0m | Provide dimension from PL to services. Large DPS service to be in own trench.
DPS Services | Storm Sanitary service | 0.3 m | For typical dual and single services for single family, duplex, and semi-detached lots. Services 50mm and smaller to be laid in same trench as storm, sanitary, and water services.
DPS Services | MH shaft | 2.0m
DPS Services | Catch Basin | 2.5m
DPS Services | Catch Basin lead | 2.5m
DPS Services | Storm and Sanitary Main | 1.5m (2.5m preferred) | For small services only (50mm and smaller). When paralleling.
DPS Services | Storm and Sanitary joint | 1.5m | Clearance is from joint, not centre of fitting (tee, cross, bend, etc.)
DPS MH | Sanitary & Storm Main | 2.5m
Valve | CB lead | 3.0m
Infrastructure with a thrust block (reducer, tee, cross or bend) | Drainage Infrastructure or non-potable water infrastructure | 1.5m
Subdomain: General / EPCOR Water (Volume 4)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance *(Unless otherwise specified) | Notes
DPS Main/Branch | Watermain | 2.5m (preferably 3.0m) | Additional clearance may be required at the Engineer's discretion, including when pipe diameters are greater than 300 mm. | District Energy Sharing Systems Standards, 4
DPS Main/Branch | Watermain | 0.3 m when crossing under DPS main/branch 0.5 m when crossing over DPS main/branch | The DPS main should have the following clearances: 0.3 m when DPS is crossing under water main 0.5 m when DPS is crossing over water main (measured from water main crown to DPS invert) It is preferred that water mains cross over non-potable mains when possible.
DPS Main/Branch | Watermain service | 2.5m (preferably 3.0m) | When paralleling main
DPS MH | Watermain | 2.5m
Oversized MH (Ø1800 & larger) | Watermain | 3.0m | From the centreline to centreline (DPS mains or branch <= 600 mm)
DPS Service Crossing | Watermain | 0.15m | Vertical Crossing
DPS Service | Large water service, Ø100 & larger | 3.0m | Provide dimension from PL to services. Large water DPS service to be in own trench.
DPS Service | Water Services | 0.3m | For typical dual and single services for single family, duplex, and semi-detached lots. Services 50mm and smaller to be laid in same trench as storm, sanitary, and water services.
DPS MH Shaft | Water Services | 2.0m
DPS Main/Branch | Water Services | 1.5m (2.5m preferred) | For small services only (50mm and smaller). When paralleling.
DPS joint | Water Services | 1.5m | Clearance is from joint, not centre of fitting (tee, cross, bend, etc.)
DPS Service | Hydrants | 2.5m
DPS Service | Infrastructure with a thrust block (reducer, tee, cross or bend) | 1.5m
DPS Service | Water Joint | 1.5m | Clearance is from the joint not from the center of fitting (tee, cross, bend, etc.). Clearance also applies to tie in joints (i.e. plugs after BVs). If a DPS main is crossing a WM it needs to be 1.5 m from any water joints.
DPS Service | Water mainstop | 0.3m
Subdomain: Landscaping (Volume 5)*
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
All DPS infrastructure | Soil cells | 1.5m (2.5 preferred) | Soil cells not permitted above DPS Mains/Branches | District Energy Sharing Systems Standards, 5
DPS Main/Branch, Services, Manual air vents, MH | Fence | 1.2m | For fencing on private property, offset for fencing on public property will be at 1.2m or greater, at the discretion of the City
DPS Main/Branch, Services, Manual air vents, MH | Deciduous tree | 1.8m | Ensure that these dimensions are measured from the actual service locations and not the property line.
DPS Main/Branch, Services, Manual air vents, MH | Coniferous tree | 3.5m | Ensure that these dimensions are measured from the actual service locations and not the property line.
Valve, curb cock (CC), DPS Main/Branch, Manual air vents, MH | Movable street and parks furniture including but not limited to benches, tables, and waste receptacles | 1.5m
DPS Valve, DPS curb cock (CC), DPS Main/Branch, manual air vents, MH | Immovable street and parks furniture including but not limited to signs, public art, and retaining walls | 3.0m
Subdomain: Streetlighting (Volume 6)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
DPS Main/Branch, Services, Manual air vents, MH | Streetlight pole (centre of pole) | 1.8m | Edge to edge with pedestal, transformer, telecommunication cubicles & streetlightlight poles | District Energy Sharing Systems Standards, 6
DPS services | Streetlight pole (centre of pole) | 1.8m
DPS Main/Branch | Streetlight pole (centre of pole) | 1.8m
Subdomain: EPCOR Power (Volume 7)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
DPS Services, blow-offs, MH, Manual air vents | 1-phase pad-mounted equipment (transformers) | 4.5m | This is the typical oﬀset. However, deviation from this oﬀset may be required at the discretion of EPCOR D&T and will be determined during Engineering Drawing review. | District Energy Sharing Systems Standards, 7
DPS Services, blow-offs, MH, Manual air vents | 3-phase pad-mounted equipment (transformers) | 5.0m | This is the typical oﬀset. However, deviation from this oﬀset may be required at the discretion of EPCOR D&T and will be determined during Engineering Drawing review.
DPS Services | Power services and Power Cables Paralleling Water Service | 1.8m
DPS Valves and DPS curb cocks | Power cables <= 40 kV | 1.0m | Minimum distance between CC and any power cables. Telecommunication cables, gas mains, duct lines
DPS Valve or DPS appurtenances is crossed on both sides | Power cables <= 40 kV | 1.8m
DPS Valve casings | Pad-mounted equipment | 1.5m | Edge to edge
DPS MH | Main power cable and duct bank | 3.0m | See EDTI Standard for Trenching Around Hydrants for reduced clearances (Volume 7: EDTI Standards)
DPS MH | Power cables <= 40 kV | 3.0m | 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
DPS Main/Branch | Secondary Power Cable (<=750 V) | 2 m from edge of pipe
DPS Main/Branch | Primary Power Cable (<=40 kV) | 4 m from edge of pipe | Primary power to be located on opposite side of the road unless power is in a four party trench or otherwise approved by the Engineer.
DPS Main/Branch | High Voltage Power Cable (>40 kV) | See Notes | To be designed based on safe limits of approach and excavation allowance.
DPS Main/Branch | Pad-mounted equipment | 3.0m | If DPS Main runs in the boulevard, deviation from this oﬀset may be required at the discretion of EPCOR D&T and will be determined during Engineering Drawing review.
All DPS infrastructure | Grounding rods | 1.8m
Subdomain: Gas
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
DPS Main/Branch | Gas main | 1.8m |  | District Energy Sharing Systems Standards
DPS Valve or curb cock (CC) | Gas mains or ductlines | 1.0m
DPS Valve or DPS appurtenances is crossed on both sides | Gas mains or ductlines | 1.8m
DPS MH | Gas mains or ductlines | 1.5m | 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
DPS Services | Gas services and gas crossings | 1.8m
DPS Services | Gas mains or ductlines | 1.8m
Subdomain: Telecommunications
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
DPS Main/Branch | Telecommmunication cable, cubicles, poles and pedestals | 1.8m |  | District Energy Sharing Systems Standards
Valve or curb cock (CC) | Telecommmunication cable | 1.0m
DPS MH | Telecommmunication cable | 1.5m | 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
DPS Valve or DPS appurtenances is crossed on both sides | Telecommmunication cable | 1.8m
DPS Services | Telecommmunication cable, cubicles, poles and pedestals | 1.8m
Subdomain: General /DPS
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance *(Unless otherwise specified) | Notes
DPS Main/Branch | DPS Main/Branch | Refer to DPS Standard Detail C-15 | Clearance between supply and return mains | District Energy Sharing Systems Standards
DPS Service Connection at the Main/Branch | To other connects including adjacent fittings, valves, etc. | 0.6m
ADDITIONAL NOTES
Blatchford has unique offsets, the actual offsets will be determined and reviewed at the time of design review
*DPS Standards are currently required only for City of Edmonton (capital) projects.

## Landscaping (including Off-Leas
Domain: Landscaping (Volume 5) (SEE ADDITIONAL NOTES AT THE BOTTOM)
Subdomain: Complete Streets and Roadways (Volume 2)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes | Data Source (Volumes from Standards)
Trees | Face of Curb (Local) | 1.0m, 1.25m preferred | Trees to be placed in line with or further from Face of Curb than Streetlight Poles. | 2,5
Trees | Edge of Sidewalk, Walkway, Driveway, and Shared-Use Path | 1.0m, preferred 1.5m
Trees | FOC (Collector) | 1.25m / 1.65m | 1.25 m ROW < 20m, 1.65 m ROW > 20m. Trees to be placed in line with or further from Face of Curb than Streetlight Poles.
Trees | FOC (Arterial) | 2.0m | Trees to be placed in line with or further from Face of Curb than Streetlight Poles.
Trees | Edge of commercial or industrial access | 1.5m
Trees | Stop signs and yield signs | 3.5m
Trees | All other signs | 2.0m
Trees | Transit zones/bus pads | 3.5m | In addition to the 3.5 m clearance, ensure trees do not create sightline obstructions for vehicles approaching transit zones.
Trees | Intersection | 15m
Trees (in walkway or shared-use path ROW) | Property line | 1.0m
Trees (in boulevard) | Property line | 1.0m
Deciduous trees (in open parkland) | Property line | 2.5m | From centre of tree, in open parkland where there is turf between the fence and the tree rather than a bed.
Coniferous trees (in open parkland) | Property line | 2.5m | From edge of mature spread of tree, in open parkland where there is turf between the fence and the tree rather than a bed.
Shrubs | Edge of Sidewalk, Walkway and Shared-Use Path | 0.5m | Shrubs at maturity.
Mulched beds | Boulevard curb | 2.5m | Within boulevard curb along arterial and collector roadways.
Benches | Back of walkway | 1.0m
Litter receptacle | Edge of Walk | 0.6m
Picnic Table | Back of walkway | 1.0m
Subdomain: EPCOR Drainage (Volume 3)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Trees | Storm and sanitary services | 1.8m |  | 3,5
Trees | Storm and sanitary manholes | 1.8m
Subdomain: EPCOR Water (Volume 4)****
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Soil cells | All water infrastructure | See Volume 4 Section 1.15 |  | 4,5
Fence | Valve, hydrant, curb cock (CC), or watermain | 1.2m | For fencing on private property, offset for fencing on public property will be at 1.2m or greater, at the discretion of the City
Deciduous tree | Watermains, services, manual air vents | 1.8m | Ensure that these dimensions are measured from the actual service locations and not the property line.
Coniferous tree | Watermains, Services, manual air vents | 3.5m | Ensure that these dimensions are measured from the actual service locations and not the property line.
Deciduous tree | Hydrant | 3.5m
Coniferous tree | Hydrant | 7.0m
Shrubs | Hydrant | 1.0 m behind hydrant and 1.5 m on either side of the hydrant (extending to road)
Movable street and parks furniture including but not limited to benches, tables, and waste receptacles | Valve, hydrant, curb cock (CC), or watermain | 1.5m
Immovable street and parks furniture including but not limited to signs, public art, and retaining walls | Valve, hydrant, curb cock (CC), or watermain | 3.0m
Provide a dimension from the landscaping element to the water appurtenance if: Within 3.0 m of water service Within 5.0 m of valve, hydrant or curb cock or any other infrastructure
Subdomain: Landscaping (Volume 5)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Shrub beds and planting beds | Shrub bed, fence, furniture, buildings, trees, and any other obstruction | 2.5m |  | 5
Shrub beds, planting beds, and trees | Any play space envelope (playground equipment and splash parks) | 5m
Shrub beds and planting beds | Edge of bed | 0.5m | Must be 500 mm (0.5 m) of mulched space between the edge of the mature shrub and the edge of the bed
Coniferous Tree | Edge of bed | 0.5m | Must be 500 mm (0.5 m) of mulched space between the edge of the mature confirerous tree and the edge of the bed
Litter receptacle | Bench | 3.0m
Subdomain: Landscaping Offleash Areas (Volume 5)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Offleash Area | Residential Areas and cemeteries (property line) | 100m | Unless separated a berm, fencing, trees or other mitigation measures and at the discretion of the City. | N/A (these specific offsets in Table of Offsets only)
Offleash Area | Arterial roads | 50m | Unless separated by fencing or other mitigation methods and at the discretion of the City
Offleash Area | Golf Courses and public areas that attract high concentrations of people | 50m | Unless separated by fencing or other mitigation methods and at the discretion of the City
Offleash Area | Multi-use trails and equestrian trails | 25m | Unless separated by fencing or other mitigation methods and at the discretion of the City
Offleash Area | School grounds or play areas and associated walking routes | 25m | Unless separated by fencing or other mitigation methods and at the discretion of the City
Offleash Area | Pools, splash parks, sports fields, and picnic areas | 25m | Unless separated by fencing or other mitigation methods and at the discretion of the City
Offleash Area | Natural areas, wildlife corridors, and other environmentally sensitive areas | Determine case by case | As determined on a case by case basis with the City
Subdomain: Streetlighting (Volume 6)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Trees | Streetlights and power poles | 3.0m |  | 5,6
Trees | Streetlight cable | 1.0m | For arterial road boulevards
Subdomain: EPCOR Power (Volume 7)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Trees | Main power trench | 1.0m | Measured from the main power cable. | 5,7
Trees and shrubs | 3-phase switching cubicle | 3.0m on each side where doors open | From edge of base
Trees and shrubs | Transformer | 2.0m on sides 3.0m in front of doors 1.5m behind base | Measured from edge of base Minimum 3.0 m clearance in front of doors required for hot stick operation Measured from edge of base
Trees and shrubs | Power crossings | 1.0m | Measured horizontally offset from the power crossing alignment
Trees and shrubs | 1-phase switching cubicle | 3.0m front 4.0m sides 2.5m behind base | From edge of base
Landscaped road island | Power crossings | SEE NOTES | See Note 1 below
Landscaped road island | Pad-mounted equipment | SEE NOTES | See Note 1 below
Subdomain: Gas and Pipelines
Trees | Contact the utility for setbacks
Trees, shrubs, shrub and planting beds | Pipelines | Planting distances from low, intermediate and high-pressure pipelines are to be observed as dictated by the Pipeline Authority. |  | N/A
Subdomain: Telecommunications
Trees | Contact telecomm company for setbacks |  |  | N/A
ADDITIONAL NOTES
*For deciduous tree(s), all measurements from centre of tree(s), for coniferous trees all measurements are from the edge of the mature spread, unless stated explicitly otherwise
** In general, setback distances apply to the majority of tree and tree form shrub species. However, certain species require different setbacks, such as those trees with suckering root systems or large hanging canopies (i.e. Poplars and Willows). Planting Populus spp. on parkland adjacent to private property is generally not recommended. However:
- Should Northwest Poplar, Balsam Poplar and Cottonwood be referenced, the minimum setback distances from private property lines shall be 15m due to root encroachment concerns. | - Should Northwest Popular, Balsam Popular and Cottonwood be referenced, the minimum setback distances from hard surfaces shall be 10m, unless special construction details are used. | - All other Populus spp., including columnar varieties, shall have a minimum setback of 10m from private property lines and 5.0m from hard surface areas where sub surface compaction has occurred.
- Some allowances may be made at the discretion of Forestry at th City if there is special construction mitigation in place, such as a root barrier.
*** Some offsets related to constrution practices (not design offsets) are provided in Volume 5: Landscaping. These must be adhered to by the Developer, Contractor, and Consultant. See Volume 5: Landscaping "Trees and Shrub Planting Setbacks" for further information.
**** Dimension symbol and legend can be used instead of dimension line to avoid clutter.
Note 1: See the City of Edmonton Design and Construction Standards Volume 5 – Landscaping …shallow utilities shall not be placed in Landscaped Road Islands. Written permission for power crossings or pad mounted equipment in Landscaped Road Islands is the responsibility of the developer. Ducts must be continuous and cannot have trees within 1.0 m of the duct. Other plantings such as small shrubs or flowers would be allowed over top of the crossing.
Distances from overhead power utilities shall be as per the requirements established by the Utility Authority.

## Streetlighting
Domain: Streetlighting (Volume 6)*
Subdomain: Complete Streets (Volume 2)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes | Data Source (Volumes from Standards)
Streetlight Pole | FOC | 1.25m along Local Streets; 1.25m along Collectors; 2.0m along Arterials; 2.6m for monowalks along Local and Collector Streets 3.0m for monowalks adjacent to School Sites |  | 2,6
Streetlight Pole | Edge of sidewalk or walkway | 0.5m , preferred 1.0m
Streetlight Pole | Edge of shared-use path | 0.5m, preferred 1.5m
Streetlight Pole | Intersection | 0.9m
Streetlight Pole | Driveway (Residential) | 0.5m with standard base and 0.75m with utility box | Edge of driveway
Streetlight Pole | Driveway/Access (Commerical or Industrial) | 1.5m | Edge of access
Multiparty trench | FOC | 2.5m | Centerline of trench
Subdomain: EPCOR Drainage (Volume 3)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Streetlights and power poles | Storm and sanitary services | 2.0m |  | 3,6
Subdomain: EPCOR Water (Volume 4)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Streetlight Pole (centre of pole) | Hydrant | 1.8m | Edge to edge with pedestal, transformer, telecommunication cubicles & streetlightlight poles | 4,6
Streetlight Pole (centre of pole) | Water services (50mm and smaller) | 1.8m | Water services 100mm and larger to be treated as watermains
Streetlight Pole (centre of pole) | Watermain | 1.8m
Subdomain: Landscaping (Volume 5)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Streetlight Pole | Trees | 3.0m |  | 5,6
Streetlight Cable | Trees | 1.0m | For arterial road boulevards
Subdomain: EPCOR Power (Volume 7)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Streetlight Pole | Primary or secondary cables | 1.0m / 0.3m | 1.0 m clearance required if streetlighting is installed after power is installed. 300 mm clearance required if streetlighting is installed at the same time as the power is installed. See standard for trenching around street light pole bases (Volume 7: EPCOR D&T) | 6,7
Streetlight Pole | Power crossings | 1.5m | To the closest power crossing duct
Main streetlight trench | Pad-mounted equipment | Common trench | See base standards and trough standards (Volume 7: EPCOR D&T)
Subdomain: Gas
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Streetlight Pole | Gas crossings and lines | 1.0m |  | 6
Subdomain: Telecommunications
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Streetlight Pole | Telecommunication lines and pedestals | 1.0m |  | 6
*All measurements from centre of pole

## EPCOR Power
Domain: EPCOR Distribution and Transmission (Volume 7) (SEE ADDITIONAL NOTES AT THE BOTTOM)
Subdomain: Complete Streets and Roadways (Volume 2)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes | Data Source (Volumes from Standards)
Transformer | Corner cut | 6.0m |  | 2,7
Transformer | FOC | SEE NOTES | Offset is required. See the specific and applicable cross-section(s) found in Complete Streets Design and Construction Standards.
Transformer | Residential driveways | 2.0m | From edge of equipment to driveway
Transformer/Switching cubicle | Bus stop pad | 3.0m | From edge of bus pad to edge of base
Transformer/Switching cubicle | Road crossing | 3.0m | From centre to closest duct in crossing
Transformer/Switching cubicle | Intersection edge of pavement | 15.0m
Transformer/Switching cubicle | Commercial/Industrial access edge of pavement | 10.0m
Pad-mounted equipment | Edge of walkway property line | 3.0m | From edge of equipment to edge of walkway property line
Pad-mounted equipment | Transportation control devices and signs | 3.0m | From edge of pad
1-phase or 3-phase cubicle | Corner cut | 30.0m
Multiparty Trench | FOC | 2.5m | Centerline of trench
Main power/multiparty trench | Property Line | 1.0m | Actual required minimum offset may change depending on sidewalk type and alignment of shallow utilities.
Power crossings | Bus stop pad | 3.0m | From edge of bus pad to crossing
Power crossings | Corner cut | 3.0m
Subdomain: EPCOR Drainage(Volume 3)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Main Power Trench | Drainage/Sanitary Main, Catch basin, manhole, vault other large drainage structure | 2.0m | Troughed to 1.5 m either side of catch basin if less than 2.0 m | 3,7
1-phase pad-mounted equipment | Manhole, catch basin, storm and sanitary services | 4.5m | 3.0 m is required from the ground grid to the other utility
3-phase pad-mounted equipment | Manhole, catch basin, storm and sanitary services | 5.0m | 3.0 m is required from the ground grid to the other utility
Power crossings | Catch basin, storm and sanitary services | 3.0m | Crossings in roadways must be 3.0 m from catch basins
Subdomain: EPCOR Water (Volume 4)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
1-phase pad-mounted equipment (transformers) | Water services and hydrants/flush points/air vents | 4.5m |  | 4,7
3-phase pad-mounted equipment (transformers) | Water services and hydrants/flush points/air vents | 5.0m
Power services and Power Cables Paralleling Water Service | Water services (50mm and smaller) | 1.8m | Clearance is from the actual water service location, not from the water service symbol Water services 100mm and larger to be treated as watermains
Power cables <= 40 kV | Valves and curb cocks | 1.0m | Minimum distance between CC and any power cables. Telecommunication cables, gas mains, duct lines
Power cables <= 40 kV | Valve or water appurtenances is crossed on both sides | 1.8m
Pad-mounted equipment | Valve casings | 1.5m | Edge to edge
Power cables <= 40 kV crossing between control valve and hydrant | Hydrants with control valves more than 2m from hydrant | Hydrants: 3m Valves 1.0m | Hydrant: 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
Main power cable and duct bank | Hydrants | 3.0m | See EDTI Standard for Trenching Around Hydrants for reduced clearances (Volume 7: EDTI Standards)
Power cables <= 40 kV | Hydrants | 3.0m | 1.0m is allowed if encased in wood, trough to 1.5m on each side of hydrant
Secondary Power Cable (<=750 V) | Water Main | 2 m from edge of pipe | Water services 100mm and larger to be treated as watermains
Primary Power Cable (<=40 kV) | Water Main | 4 m from edge of pipe | Primary power to be located on opposite side of the road unless power is in a four party trench or otherwise approved by the Engineer.
High Voltage Power Cable (>40 kV) | Water Main | See Notes | To be designed based on safe limits of approach and excavation allowance.
Pad-mounted equipment | Watermain | 3.0m
Grounding rods | All water infrastructure | 1.8m
Power Poles and Pole Anchors | Watermain and Water services | 1.8m
Subdomain: Landscaping (Volume 5)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Main power trench | Trees | 1.0m | Measured from the main power cable. | 5,7
1-phase switching cubicle | Trees and shrubs | 3.0m front 4.0m sides 2.5m behind base | From edge of base
3-phase switching cubicle | Trees and shrubs | 3.0m on each side where doors open | From edge of base
Pad-mounted equipment | Landscaped road island | SEE NOTES | See Note 1 below
Transformer | Trees and shrubs | 2.0m on sides 3.0m in front of doors 1.5m behind base | Measured from edge of base Minimum 3.0 m clearance in front of doors required for hot stick operation Measured from edge of base
Power crossings | Trees and shrubs | 1.0m | Measured horizontally offset from the power crossing alignment
Power crossings | Landscaped road island | SEE NOTES | See Note 1 below
Subdomain: Street Lighting (Volume 6)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Pad-mounted equipment | Main streetlight trench | Common trench | See base standards and trough standards (Volume 7: EPCOR D&T) | 6,7
Primary or secondary cables | Streetlight Davit Poles or Contactors | 1.0m / 0.3m | 1.0 m clearance required if streetlighting is installed after power is installed. 300 mm clearance required if streetlighting is installed at the same time as the power is installed. See standard for trenching around street light pole bases (Volume 7: EPCOR D&T)
Power crossings | Streetlight Davit Poles or Contactors | 1.5m | To the closest power crossing duct
Subdomain: Gas
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Pad-mounted equipment | Gas crossing | 3.5m | From centre of equipment (minimum 2.0 m grom ground grid) | 7
Pad-mounted equipment ground grid | Main gas trench | 1.0m | From ground grid to gas line trench
Main power trench | Main | 1.0m | Parallel, see Note 2 below
Power crossings | Main | 1.0m | Parallel
Power crossings | Main or service | 300mm | Without mechanical separation, see Note 3 below
Subdomain: Telecommunications
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Pad-mounted equipment | Main communications trench | Common trench | See base standards and trough standards (Volume 7: EPCOR D&T) | 7
Pad-mounted equipment | Communications pedestals | 3.0m | Minimum 3.0 m from case of transformer or switching cubicle to case of pedestal, see Note 4 below
Primary or secondary cables | Communication vault | 300mm | Minimum clearance between edge of communication vault and edge of primary or secondary cable
Power crossings | To the closest power crossing duct | Power crossing | Communications equipment
Subdomain: Pipeline Rights-of-Ways (Other Than ATCO IP for Servicing the Subdivision)
Domain Infrastructure | Subdomain Infrastructure | Minimum Clearance | Notes
Pad-mounted equipment | From edge of right-of-way | 10.0m | From edge of pipeline right-of-way to edge of ground grid | 7
Power crossings | From edge of right-of-way | 5.0m | Power crossing ducts perpendicular to pipeline are to be extended a minimum of 5.0 m from edge of right-of-way to end of crossing duct
ADDITIONAL NOTES
These are preferred minimum horizontal clearances. Consult with EDTI Land Servicing for discussion of the possibility of any deviation to these approved clearances due to specific circumstances.
Clearances are from centre to centre of furniture, trench or duct unless otherwise noted.
Note 1: See the City of Edmonton Design and Construction Standards Volume 5 – Landscaping …shallow utilities shall not be placed in Landscaped Road Islands. Written permission for power crossings or pad mounted equipment in Landscaped Road Islands is the responsibility of the developer. Ducts must be continuous and cannot have trees within 1.0 m of the duct. Other plantings such as small shrubs or flowers would be allowed over top of the crossing.
Note 2: If it is mutually agreed that gas is in the same trench as power, refer to refer to EDTI Underground Distribution Standard 6000070046001 for the typical roadway cross-section to use.
Note 3: Where mutually agreed, an approved method of mechanical separation could be used to reduce the crossing from 300 mm (i.e. 5 Party Trenching, using a sleeve, fastened to the I.P. gas line, as mechanical separation and 100 mm of sand between the sleeve and the power cable.).
Note 4: If communications pedestals are placed with 3.0 m from the edge of the ground grid of pad mounted power equipment, the two pieces of equipment will be bonded. A detail drawing is required.
Note 5: Landscaping clearances are for work on City of Edmonton road allowances only. Landscaping clearances on EDTI utility rights-of-way (URW) are as per the URW documents.

## Consolidated Design Exception F
City of Edmonton Consolidated Design Exception Form
PROJECT INFORMATION
Project Title
Project Limits, Address, LDA Number, Stage Number, Contract Number
WR# or WO# (if applicable)
Design Engineer / P.Tech
Project Manager
Project Type |  | Describe the type of civil works project that requires a design exception (i.e. electrical upgrade, drainage installation, road works, etc.)
Applicable Volume for Exception (Separate form must be submitted for each volume): |  | FALSE | Volume 2 | FALSE | Volume 6
|  | FALSE | Volume 3 | FALSE | Volume 7
|  | FALSE | Volume 4 | FALSE | Volume 8
|  | FALSE | Volume 5 | FALSE | Other:
Exception Requested |  | Describe the exception you are requesting and identify the standards document (most recent published version/volume), specific text, drawings, and/or section you are requesting exception from? Indicate the design element or combination of elements which the design exception is proposed for (e.g. curb radius; lane width; offset; etc.).
DESIGN EXCEPTION INFORMATION
Background, Location, Context |  | Explain the type of exception (e.g. lack of required separation between infrastructure, minimum dimensions not satisfied, etc.) and where it will apply (e.g. located within the Road Right of Way on the north side of street between cross roads; intersection; intersection quadrant; neighbourhood; or within walkway between lot/block numbers). Include a site plan as an attachment. Describe the context of the exception (e.g. adjacent land use, local conditions, street classification, anticipated infrastructure demands, previous projects, or existing design and/or construction components that do not meet current standards)?
Rationale |  | What is the rationale for the design exception? Include any supporting documents as applicable such as 1) calculations and/or modeling results; 2) supporting detailed engineering drawings (e.g. utilities drawings, plan & profiles, cross-sections, swept path analysis, etc. as attachment pages); and 3) previous documents, amendments, or approvals that provide further justification for the requested exception.
Alternatives Considered |  | What alternatives (if any) were considered in the decision? What is the benefit of and what are the impacts avoided with the identified solution(s) over other alternatives considered?
Potential Impacts and Risks |  | What are the potential impacts and risks? Evaluate the potential risks associated with the exception (e.g. health and safety, property damage, etc.), including potential impacts to the City/EPCOR related to the service life of infrastructure, operation and maintenance requirements, and overall performance. Include safety risk level (e.g. margina, nominal, substantive).
Mitigation Measures |  | What proposed/additional mitigation measures are being included to reduce and offset the potential impacts and risks of the exception (e.g. signage, vehicle restrictions, etc.)? Identify each risk and their details, including supporting calculations (be conservative in approach).
Supporting Information (if applicable) |  | What (if any) additional supporting documents, data, or technical resources were used in making the decision (e.g., research papers, best management practices, other municipal/provincial/federal guidelines, etc.)? For ease of review, please provide copies or links to supplementary reports, as well as original and proposed designs.
SUBMITTED BY:
Name |  |  | Authentication (required) |  | Validation (required)
Title
Company
Primary Contact
Date of Submission
Inspector Name (if applicable)
I certify the information provided on and attached to this application is accurate and complete. All drawings, documents, details, specifications and supporting information contained in this application pertain to the project that is the subject of this application.
Signature(s) | Developer/Consultant Representative | Inspector (if applicable)
Date(s)
Internal City / EPCOR Use Only
ACCEPTANCE / REJECTION
Decision | Accepted | Rejected
| FALSE | FALSE
INTERNAL SIGN OFF
| Designer | Engineer | Manager | Comments
Name
Title
Department
Primary Contact
Date
Signature
Sign Off Requirements for Acceptance: | Volume 2: | Design Reviewer, Supervisor (Manager)
| Volume 3: | Design Reviewer, Engineering Reviewer, Land Servicing Manager
Volume 4:
Volume 5:
Volume 6:
Volume 7:
Volume 8:
Disclaimer: Unless prior written approval has been obtained, developers or their representatives must follow and meet all of the requirements within the applicable design standards. This exception approval request is project specific and does not apply to other projects. All other requirements not varied by this exception shall continue to apply, including, but not limited to, other applicable guidelines, standards, codes, agreements, and contracts.